## Fire Protection Impairment

## Permit

| Organisation |  |
| --- | --- |
| Location |  |
| Impairment Authoriser |  |
| Phone Number/email |  |

#### A.  IMPAIRMENT

| Date and time |  |
| --- | --- |
| Anticipated Duration |  |
| Authorised by: |  |

| Type of equipment impaired |
| --- |
| 1 Sprinkler Riser(s) / System (s) | Y/N | 5 Hydrant / Hose reel main | Y/N |
| 2 Fire Pump | Y/N | 6 Fire Detection System | Y/N |
| 3 Water Tank | Y/N | 7 Automatic gas extinguishing system | Y/N |
| 4 Public Water Supply | Y/N | 8 Other (e.g. smoke vents, shutters etc.) | Y/N |

Affected area (indicate area and equipment involved)

Cause of the impairment

| Precautions taken (see explanations overleaf) |
| --- |
| 1 Management notified | Y/N | 6 Smoking forbidden | Y/N |
| 2 Fire teams notified | Y/N | 7 Continuous occupation of impaired area | Y/N |
| 3 Additional watchman rounds | Y/N | 8 Temporary water supply | Y/N |
| 4 Fire extinguishers available | Y/N | 9 Hazardous operations stopped | Y/N |
| 5 Hot work operations stopped | Y/N | 10 Other: | Y/N |

#### B. RESTORATION

| Date and time of restoration |  |
| --- | --- |
| Impairment Authoriser |  |

Instructions

A.	Impairment:  Please fill in part A of the form and email to Risk@protectorinsurance.co.uk if the planned impairment is expected to exceed 12 hours or if the impairment is due to actuation of an automatic protection system.

B. Restoration:  Please fill in part B of the form and email it to Risk@protectorinsurance.co.uk once the impaired system has been reinstated

Precautions to be taken in case of impairment of fire protection equipment:

Before and during works:

- Plan and prepare works to minimise the duration of the impairment;

- Avoid impairing several sprinkler risers at the same time;

- If works have to last several days consider putting the protection system back in service at night;

- Use existing sectional control valves to isolate the affected area and to keep as many protection systems as possible in service. Water supplies should only be impaired when there are no other solutions;

- Inform appropriate Management where protection is impaired to make sure loss prevention measures are strictly applied during the impairment and to postpone hazardous operations when possible;

- Notify each member of the Plant Emergency Organisation and (if applicable) the Alarm Receiving Centre, Fire Service and other interested parties;

- Forbid all ‘Hot Work’ in the impaired area;

- Enforce ‘no smoking’ regulations in the impaired portion of the plant;

- Establish a fire watch (hourly rounds at least) in the impaired area during idle times;

- Have fire extinguishers on hand throughout the duration of the impairment.

At the end of the works:

- Make sure all sprinkler and water supply valves are open and sealed or padlocked in the open position;

- Conduct a test at each sprinkler riser by opening fully the 2-inch drain valve. Pressure should not drop significantly and should quickly go back to its original position as soon as the valve is closed;

- All persons informed of the impairment should be informed of the restoration.

##### In case of problems, please contact the Risk Management Team at Protector Insurance:

##### Risk@protectorinsurance.co.uk  +44 (0) 161 274 9077